54.1.3 Communication between a remote operator workstation and the central-station company shall comply with (a) and (b) or (c) and (d) as follows:

      - There shall be primary and backup communication connections between the remote operator workstation and the central-station company shall comply with 12.1.6.

      - The workstation, router, and networking equipment necessary to support communication with the central-station company shall be powered by an uninterruptible power supply that can battery backup for the amount of time needed to transfer active alarm to another operator

      - There shall be sufficient operators on-duty and logged into the automation system, so that loss of communication between a remote operator workstation and the central-station company will not result in the loss of any signals or failure to process signals in the manner and timeframes required by this Standard.

      - System and workstation monitoring shall be in place to ensure 99.95% connectivity between workstations and the monitoring center during the time an operator is handling alarms. Connectivity is to be measured as all operator alarm handling time during a rolling 30-day period. Central-station company shall maintain and retain data to substantiate that this connectivity requirement is met.